Section 160.40  Location of Tanks – Distance Between Aboveground Tanks

a)	The minimum distance from tanks to adjacent tanks shall be as follows:

| Tank Capacity (Gallons) | Minimum Distance (Feet) |  |
| --- | --- | --- |
| 24,000 or less |  | 5 |
| 24,001 to 48,000 |  | 10 |
| 48,001 to 75,000 |  | 13 |
| 75,001 to 100,000 |  | 15 |
| Over 100,000 |  | One Tank Diameter |  |

b)	If tanks are of different capacities, the capacity of the larger tank shall govern its distance to adjacent tanks.

c)	Existing tanks of under 24,000 gallons shall maintain a minimum distance of at least 3 feet.

(Source:  Amended at 9 Ill. Reg. 10012, effective October 1, 1985)