Section 200.10  Storage and Handling of Liquefied Petroleum Gases

Requirements for the storage and handling of liquefied petroleum gases as contained in the 2011 Edition of NFPA 58 (Liquefied Petroleum Gas Code) are mandatory with the following additional requirements:  The pressure relief valve discharge on each aboveground container of more than 2000 gal. water capacity shall be piped vertically upward to a point at least 7 ft. above the top of the container, and the discharge opening shall be unobstructed to the open air.

(Source:  Amended at 36 Ill. Reg. 8735, effective August 1, 2012)